| Daily Work Report |
| --- |
| Site: | Kaliningrad TEC 2 | Unit Ser. No: | GT 21 |
| Date: | 15th Sept 2015 | Weather Conditions: | NA, inside |
| Personnel: | 3 Sulzer + 2 Interpreter + 11 Bem | Safety Incidents: | No |

Work Accomplished

Day shift No work permit until 11:00 for welder exhaust Welding exhaust casing finished at 18:00 Weld drain pipe (new dilo coupling) left combustion chamber Final adjustment turbine vane carrier Install top and bottom centre pin TVC Install side adjusters TVC Final measurement first and fourth stage turbine blade Work on translation protocols. Night shift Drilled out sheared stud on barring gear manhole door. Fitted door. Cleaned out compressor discharge had inspected by client and closed door. Bolts tightened. Swept out exhaust. Hoovered out combustion chambers. Both doors closed but only on one bolt. Measured Vla1. Cleaned out inlet and had inspected. The client is going to mop out the chamber.

Work Scheduled for upcoming day

Pre-commissioning combustion chamber instrumentation Dye check exhaust casing Clean and final closing inspection exhaust Clean and final closing inspection both combustion chambers Finalize last assembling protocols

Upcoming Requirements ( Rotec) Welder for the sight glass cooling air pipe left side CC Upcoming Requirements (Sulzer)

Additional Information

Safety: